FIKES EPC Fault Finding

This help sheet is to be used in combination with The Fike Manual P/N E06-053 which can be found on the shared drive inside folder ‘12. Useful Information and Drawings’.

- TAKE PHOTO OF DIGITAL DISPLAY OR RECORD THE THREE DISPLAYED DIGITS. – Disarming will create a new code so this first step is important.

- Call Fikes to make them aware we are having issues with the Fikes unit.  This will allow Fikes to get you in touch with the correct person who can advise over the phone.

Fikes Office	 	01622 677081   	*CALL FIRST or email*

Service.UK@Fike.com

Mathew Tonks 	07733 363 170

______________________________________________

Unit interrogation of the Annunciator Module:

Pressing a single button will show current mode.

Press both buttons to change operating modes.

Procedure:

- Press both buttons together – hold until unit beeps

- Use left key to scroll through modes

- Use right key to select mode (enter)

- Menu will timeout after 20 seconds

The following modes are available:

STA	- Status

HIS	- History

DET	- Pressure reading

EPC	- EPC enable / disable

PSU	- On / Off

RC8	- RC8 enable / disable

Do not enter EPC, PSU or RC8 menus as this could cause an emergency stop of the unit.

If this happens, hold both buttons again to re-select another mode or wait for a timeout

MODE: STA 	– Status:

Displays the current status of the modules.  See page 13 of the manual for further information.

Fist number on display is the unit:

0 – Annunciator Module

1 – EPC 1

2 – EPC 2

3 – EPC 3

4 – EPC 4

9 – PSU

The second two numbers indicate status.  See page 14 of the manual for further information.

The EPCs are numbered 	1 2 - Head
and 				3 4 - Boot

MODE: HIS 	– History:

Displays the last 40 instances of fault history.  The most recent being at the top.  When you hit the top of the list, three dashes will be displayed on the top of the digital display, when you hit the bottom of the list, three dashes will be displayed on the bottom of the display.

Press the left button to advance and the right to step back in history list.

Press both buttons to return to the top of the list.

Note, this also remembers when the unit has been powered down each evening and displays it as a fault. 104, 204, 304, 404 all log as Trouble on output circuit, but this is generated when the units are shut down of an evening.

See page 21 of the manual for further information on fault codes.

Examples of codes are:

X01 – System armed and healthy

X09 – System disarmed 		Generated as part of the correct shutdown procedure.

X04 – Trouble on output circuit 	Generated as part of the correct shutdown procedure.

X07 – Supervisory input active	Check explosion sensors (See ‘SIM’ units below).

MODE: DET 	– Pressure readings:

This presents live readings from the external pressure detectors.

First Digit : Location of sensor	2nd Digit: Detector live pressure value

1 = Elevator Boot			HEX Code [see table]

5 = Elevator Head			HEX Code [see table]

7 = Upper Garner			HEX Code [see table]

Hex codes should be between 78 and 85 as per the table on page 23 of the manual.  Detectors should read atmospheric value of 0mbar [HEX 7F]. Warning occurs +40mbar [Hex 90]

SIM Units – bottom of head house panel

There are also four ‘SIM’ units at the bottom of the Fike panel.  These monitor the circuit on each of the Main Elevator explosion panels on the 10th floor Head House.

There are four sensors for each elevator connected up in series in a normally closed circuit.

A red indication light on the ‘SIM’ unit represents a fault with the explosion panel circuit.

An amber light indicates a previous fault that has rectified itself.

These faults will display as code X07 – Supervisory Input Active.  The units will disarm and not re-arm until this problem is resolved.

August 2023 PH